## Connecticut BNR facilities
Rhode Island BNR Facilities
TOWN | FACILITY NAME | FACILITY LOCATION | MAILING ADDRESS |  | PHONE #s | NPDES PERMIT # | MUNI OR PRIV WPCF | CHIEF OP/ SUPERINT | TOWN LIMITS | DESIGN or PERMIT FLOW (mgd) | RECEIVING WATER | Nitrogen Removal Processes | [8 empty] | Supplemental Carbon | [5 empty] | Notes
[12 empty] | Pre-Anoxic | Aeration Basin | IFAS Media | RBC | Step feed BNR | SBR | Ox Ditches | Post-Anoxic | BNR Filter | Acetic Acid | Glycerin | Other supplemental carbon | reclaimed methanol | Flammable Liquid Capable | Methanol
Cranston+A2:F4 | Cranston WPCF (operated by veolia Water) | 140 Pettaconsett Ave, Cranston, RI, 02920 | same as address |  | (401) 467-7210 |  | M | Earl Salisbury | 30/30 85/85 | 20 | Pawtuxet River | x | x | [5 empty] | x |  |  | x |  |  | F | F | Facility presently under construction for a plant upgrade with supplemental carbon. Use of supplemental carbon likely in 2016 and the facility is capable of using methanol. Existing supplemental carbon use is glycerin stored in totes on a temporary basis .
East Greenwich | East Greenwich WPCF |  | PO Box 11, Town Hall | East Greenwich, RI 02818 | (401) 886-8619 |  | M | Michael Pacillo | AWT see permit | 1.7 | Greenwich Cove |  |  |  | x |  |  |  |  | x |  |  |  |  | x | x | Small facility denite filter that uses methanol.
East Providence | East Providence WWTF (operated by United Water) | Crest Ave, Riverside, RI 02915 | same as address facility |  | (401) 433-6363 |  | M | David Gaipo | 30/30 85/85 | 14.2 | Providence River | x | x | x |  |  |  |  | x |  |  | F |  |  |  |  | Facility presently does not need to use supplemental carbon. If new permit limits are lowered from 8 mg/l down to 5 mg/l TN the use of glycerin is likely. Facility presently only has storage capability in totes.
Narragansett Bay Commission Providence | Bucklin Point WWTF | 102 Campbell Ave. East Providence, RI 02905 | Same as facility address |  | (401) 434-6350 |  | M | Tom Ciolfi | AWT see permit | 46 | Seekonk River | x | x | [5 empty] | x |  |  | x |  |  |  |  | Uses glycerin intermittently as needed. 2 (4,000 gallon) storage tanks. Facility can only use non flammable liquids.
Narragansett Bay Commission Providence | Fields Point WWTF | 2 Ernest St. Providence, RI 02905 | Same as facility address |  | (401) 461-8848 |  | M | Carmine Goneconte | N | 65 | Providence River | x | x | x |  |  |  |  | x |  |  | x |  |  | x |  | Presently using glycerin intermittently as needed. 4 (8,000 gallon) storage tanks. Facility is capable of using methanol, however is only using glycerin at the present time. Facility uses 400-500 gallons per day in the months of March- June and does not require supplemental carbon the remainder of the year. Future economic considerations will be given to methanol if the product is more cost effective over glycerin.
Rhode Island Resource Recovery Landfill | Johnstown Landfill leachate treatmet WPCF |  | 65 Shum Pike Road, Johnstown, RI 02919 |  | (401) 942-1430 |  | M/P |  | 30/30 85/85 | 0.6 | Discharge to Fields Point WWTF | [5 empty] | x | [7 empty] | x | x | New leachate pre treatment facility to start up in 2015 with limit of 10 mg/l NOx. facility will use methanol 800-1,000 gpd year round and has 2 (10,000 gallon) storage tanks. A bid for methanol will be advertised in the near future.
West Warwick | West Warwick Regional WWTF | 1 Pontiac Ave, West Warwick, RI 02893 | Same as facility address |  | (401) 822-9228 |  | M | Bernie Bishop | AWT see permit | 7.9 | Pawtuxet River | x | x | [6 empty] | x |  |  |  |  | x | x | Uses methanol in the BAF denite filter in the 100 gpd range.
Woonsocket | Woonsocket WWTF (operateed by OMI) | 11 Comberland Hill Rd, Woonsocket, RI 02895 | Samme as facility address |  | (401) 356-1468 |  | M | Kevin Dahl | AWT see permit |  | Blackstone River | x | x | [5 empty] | x |  |  | F |  |  | F | F | New process upgrade is scheduled to become operational in 2015. The Woonsocket permit is the lowest total nitrogen permit requiring a limit of 3 mg/l total nitrogen in Rhode Island. As with all direct dischargers to surface water entering Narragansett Bay the nitrogen limit is seasonal from April - October. The facility is designed to use glycerin but can be easily modified to use methanol. Start up is schuled to use glycerin however, future supplemental carbon cost economics will drive the long term supplemental carbon selection.