## Connecticut BNR facilities
Virginia BNR Facilities
TOWN | FACILITY NAME | FACILITY LOCATION | MAILING ADDRESS | PHONE #s | NPDES PERMIT # | MUNI OR PRIV WPCF | Manager | TOWN LIMITS | DESIGN or PERMIT FLOW (mgd) | RECEIVING WATER | Nitrogen Removal Processes | [9 empty] | Supplemental Carbon | [5 empty] | Notes
[11 empty] | Pre-Anoxic | Aeration Basin | IFAS Media | MBR | RBC | Step feed BNR | SBR | Ox Ditches | Post-Anoxic | BNR Filter | Acetic Acid | Glycerin | Other supplemental carbon | reclaimed methanol | Flammable Liquid Capable | Methanol
Alexandria | Alexandria Renew Enterprises | 1500 Eisenhower Ave. Alexandria, VA 22314 | same | 703-549-3381 | VA0025160 | M | Samuel Shafer or James Canaday |  | 54 | Potomac River Basin | x | x | [6 empty] | x | [5 empty] | x | x | Large methanol user with a 3 mg/l TN limit
Arlington | Arlington County WPCP | 3401 S. Glebe Road, Arlington, VA 22201 | same | 703-228-6822 | VA0025143 | M | Larry Slattery |  | 40 | Potomac River Basin | x | x | [6 empty] | x | x |  |  |  |  | x | x | Large methanol user with a 3 mg/l TN limit
Babcock & Wilcox | BWX Technologies | 1570 Mount Athos Road, Route 726, Lynchburg, VA 24504 | same | 434-522-5202 | VA0003697 | I | Chris Terry |  | 1 | Potomac River Basin | [6 empty] | x |  |  |  |  | x |  |  |  |  | Uranium processing facility that uses glycerin for nitrate reduction. High strength nitrate concentration required to be reduced to 114 mg/l total nitrogen.
Broadway | Broadway Regional WWTF | 15524 New Market Rd Broadway, VA 22853 | same | 540-896-7351 | VA0090263 | M | John Coffman | 30/30 85/85 | 2.93 | Potomac River Basin | x | [6 empty] | x | x | x |  | x |  |  |  |  | Plant uses glycerin in their Blue Water dnite filter intermittently as needed or approx. 30,000 gal annually. Nitrogen limit is 3.7 mg/l TN . This is a small flow facility that treats high strength nitrogen waste from a Tyson and a Pligrims Pride poultry processing facilitiy.
Charlottesville | RWSA Moores Creek Regional WWTP | 695 Moores Creek Lane Charlottesville,VA 22902 | same | 434-977-2065 | VA0025518 | M | Rich Gullin |  | 15 | James River basin | x | x | [6 empty] | x |  |  | x |  |  |  |  | Uses 100 gallons per day of glycerin in the post anoxic zone
Chesterfield County | Falling Creek WWTF | 2100 Station Rd. Richmond, VA 23234 | same | 804-275-0063 | VA0024996 | M | Scott Smedely |  | 10.1 | James River basin | x | x | [6 empty] | x | [5 empty] | x | x | Facility uses 350 gpd of methanol.
Chesterfield County | Proctors Creek WWTF | 1200 Coxendale Road, Chester, VA 23831 | same | 804-768-7272 | VA0060194 | M | Scott Smedely |  | 27 | James River basin | x | x | [6 empty] | x | [5 empty] | x | x | Facility uses 700 gpd of methanol
Culpeper | Culpeper WWTF | 15108 Service Lane, Culpeper, VA 22701 | same | 540-825-6060 | VA0061590 | M | Joey Blankenship |  | 6 | Rappahannock River basin | x | x | [6 empty] | x | x |  | x |  |  | x |  | Facility uses glycerin in the 2nd anoxic zone for denitrification and does not use the denite filter.
Dale City | Dale Service Corp. #1 | 15051 S. Birchdale Ave. Dlae City , VA 22193 | same | 703-590-4495 | VA0024724 | M | Norris Sisson |  | 4.6 | Potomac River watershed | [6 empty] | x | [7 empty] | x | x | facility uses methanol in the anoxic SBR cycle for denitrification.
Dale City | Dale Service Corp. #8 | 14420 Delaney Road, Dale City, VA 22193 | same | 703-590-4495 | VA0024678 | M | Norris Sisson |  | 4.6 | Potomac River watershed | [6 empty] | x | [7 empty] | x | x | facility uses methanol in the anoxic SBR cycle for denitrification.
Fairfax County | Noman Cole Pollution Control Plant | 9399 Richmond Hwy. Lorton, VA 22079 | same | 703-550-9740 | VA0025364 | M | Kailash Gupta |  | 67 | Potomac River Basin | x | x | x | [5 empty] | x | [5 empty] | x | x | Large methanol user 1,750 gpd with a 3 mg/l TN limit
Fisherville | Fisherville Regional WWTP Augusta County Service Authority | 887 Sangers Lane Staunton, VA 24401 | P.O. Box 859 , Verona, VA 24482 | 540-245-5227 | VA0025291 | M | Tony Morse Dir. Wastwater Operations |  | 4 | Potomac River Basin | x | x | [7 empty] | x |  | x |  |  | x | x | Facility uses approx. 20,000 gallons per year of glycerin
Fredrickburg | Massaponax WWTF | 10900 Hugh Cosner Dr. Fredricksburg, VA 22408 | same |  | VA0025658 | M |  |  | 9.4 | Rappahannock River basin | x | x | [6 empty] | x | x | x | x |  |  |  |  | Facility uses acetic acid or glycerin in the post anoxic zone.
Fredricksburg | Little Falls Run WWTF | 952 Kings Hwy. Fredricksburg, VA 22405 | same | 540-658-5120 | VA0076392 | M | Brian Green | AWT see permit | 8 | Rappahannock River basin | [6 empty] | x |  |  | x |  |  |  |  | x |  | Facility has denitrification filters with methanol capbility however, they are meeting TN permit of 6 mg/l without needing the filters.
Front Royal | Front Royal WWTF | Manasses Ave, Front Royal, VA 22630 | P.O. Box 1560 Front Royal, VA 22630 | 540-622-6504 | VA0062812 | M | Joe Waltz | AWT see permit | 4 | Potonac River basin | x | x | [6 empty] | x |  | x | x |  |  |  |  | Plant is under construction for a process upgrade using a activated sludge process with Bio Mag a propritary high bio mass process. The plant is installing a non flamable supplemantal carbon system but is not expecting to need to use supplemental carbon.
Hampton Roads Sanitation District (HRSD) | Nansemond | 6909 Armstead Rd. Virginia Beach, VA 23435 | 1436 Air Rail Ave. Virginia Beach, VA 23455 | 757-460-4245 | VA0081299 | M | Sharon Nicklas R. W. Lawrence |  | 30 | Lower James River | x | x | [6 empty] | x |  |  |  |  | x | x | x | Facilitity presently uses reclaimed methanol at approximately100-200 gpd.
Hampton Roads Sanitation District (HRSD) | Army Base | 401 Lagoon Rd. Norfolk, VA 23505 | 1436 Air Rail Ave. Virginia Beach, VA 23455 | 757-460-4245 | VA0081230 | M | Sharon Nicklas R. W. Lawrence |  | 18 | Lower James River | x | x | [6 empty] | x |  |  | x |  | x | x | x | Not using carbon presently but will in 2016 when upgrade is completed. They will use the most cost effective source available.
Hampton Roads Sanitation District (HRSD) | VIP Virginia Inititive Plant | 4201 PowhatanAve. Norfolk, VA 23508 | 1436 Air Rail Ave. Virginia Beach, VA 23455 | 757-460-4245 | VA0081281 | M | Sharon Nicklas R. W. Lawrence |  | 40 | Lower James River | x | x | [6 empty] | x |  |  | x |  | x | x | x | Not using carbon presently but will in 2017 when upgrade is completed. They will use the most cost effective source available.
Hampton Roads Sanitation District (HRSD) | York River | 515 Back Creek RD. Virginia Beach, VA 23696 | 1436 Air Rail Ave. Virginia Beach, VA 23455 | 757-460-4245 | VA0081311 | M | Sharon Nicklas R. W. Lawrence |  | 15 | York River | x | x | [6 empty] | x | x |  |  |  |  | x | x | Presently uses 600-650 gpd of methanol
Hampton Roads Sanitation District (HRSD) | James River | 111 City Farm Road, Virginia Beach, VA 23602 | 1436 Air Rail Ave. Virginia Beach, VA 23455 | 757-460-4245 | VA0081272 | M | Sharon Nicklas R. W. Lawrence |  | 20 | Lowe James River | x | x | [6 empty] | x |  |  | x |  |  |  |  | Does not use supplemental carbon at this time but if needed can only use non-flamable carbon sources.
Harrisonburg | North River HRRSA | 856 North River Road, Mount Crawford, VA 22841 | same | 540-434-1053 | VA0060640 | M | Robert Havener | 30/30 85/85 | 22 | Potomac River basin | x | x | [6 empty] | x | x | [6 empty] | Uses approx. 5,000 gpy of 56% acetic acid. Tried glyccerin in the past and it failed to work.
Henrico County | Henrico County WWTF | 9101 WRVA Road, Richmond, VA 23231 | same | 804-795-9302 | VA0063690 | M | James Grandstaff |  | 75 | James River basin | x | x | [6 empty] | x |  |  | x |  |  |  |  | Large glycerin uses of approx. 1000 gpd.
Hopewell | Hopewell Regional WWTF | 231 Hummel Ross Road, Hopewell, VA 23860 | same | 804-541-2210 | VA0066630 | M | Matt Ellinghouse |  | 50 | James River basin | x | x | x | [5 empty] | x | [7 empty] | A large municipal treatment facility that serves several major industrial dischargers. Treatment plant is being upgraded and will complete the upgrade in 2017. The facility does not anticipate the need for supplemental carbon in the future.
Leesburg | Leesburg WWTF | 1391 E. Market St., Leesburg, VA 20176 | same | 703-737-7092 | VA0092282 | M | Brian Bailey | 30/30 85/85 | 7.5 | Potomac River basin | x | x | [6 empty] | x | x |  |  |  |  | x | x | Uses 100 gallons per day of glycerin in the post anoxic zone
Loudon | Broadrun Water Reclamation Plant | 44966 Loudon Water Way Ashburn, VA 20147 | same | 571-291-7700 | VA0091383 | M | Michael Rumke |  | 11 | Potomac River basin | x |  |  | x |  |  |  |  | x | [5 empty] | x | x | Uses 200 gpd methanol in an MBR process.
Middle River | Middle River, Augusta County Service Authority | 828 Laurel Hill Road Verona, VA 24482 | P.O. Box 859 , Verona, VA 24482 | 540-245-5227 | VA0064793 | M | Tony Morse Dir. Wastwater Operations |  | 6.8 | Potomac River Basin | x | x | [7 empty] | x |  | x |  |  | x | x | Facility uses very little glycerin as needed approx 4,000 gallons per year
Purcellville | Basham Simms Wastewater Facility | 1001 S. 20th St. Purcellville, VA 20132 | same |  | VA0022802 | M |  |  | 1 | Potomac River basin | x | x | [7 empty] | x |  |  |  |  | x | x
Richmond | Richmond City WWTP | 1400 Brander Street Richmond, VA 23224 | same | 804-646-7864 | VA0063177 | M | Robert Steidel |  | 45 | James River basin | x | x | [7 empty] | x |  |  |  |  | x | x | large methanol users at 1,800 gpd in denitrification filters.
Tyson Foods | Tyson Foods Temperanceville | 11224 Lankford Hwy, Temperanceville, VA 23442 | same | 757-824-3471 | VA0004049 | I | Jarrod Goodman | AWT see permit | 1.25 | Eastern Shore basin | x | x | [9 empty] | x |  |  |  |  | Poultry processor uses glycerin in anoxic zone approx 100 gpd..
Tyson Foods | Glen Allen Processing Facility | 13264 Mountain Road, Glen Allen, VA 23059 | same | 804-998-8357 | VA0004031 | I | Michael Tilley |  | 1.1 | James River basin | x | x | [9 empty] | x |  |  |  |  | Poultry processing plant with a 6 mg/l TN limit that uses glycerin as a supplemental carbon source.
Verona | Stuarts Draft, Augusta County Service Authority | 391 Wayne Ave. Verona, VA 24477 | P.O. Box 859 , Verona, VA 24482 | 540-245-5227 | VA0066877 | M | Tony Morse Dir. Wastwater Operations | 30/30 85/85 | 4 | Potomac River Basin | x | x | [6 empty] | x | x |  | x |  |  | x | x | Facility uses very little glycerin as needed approx 2,000 gallons per year
Warrenton | Warrenton WWTF | 731 Frost Ave., Warrenton, VA 20186 | same | 540-347-1104 | VA0021172 | M | William Stoddard |  | 2.5 | Rappahannock River basin | x | x | [7 empty] | x |  |  |  |  | x | x
Washington DC Blue Plains | Blue Plains/DC WATER | 5000 Overlook Ave. Washington, DC 20032 | same | 202-878-4172 | DC0021199 | M | Walter Bailey |  | 370 | Potomac River | x | x | [6 empty] | x |  |  |  | x |  | x | x | Largest wastewater treament facility using methanol in the US. Recently completed a new supplemental carbon storage and pumping upgrade capable of using a number of carbon sources and will use the most cost effect product.
Waynesboro | Waynesboro WWTF | 930 Essex Ave., Waynesboro, VA 22980 | same | 540-942-6624 | VA0025151 | M | Ross Morland |  | 6 | Potomac River basin | x | x | [6 empty] | x | x |  | x |  |  | x |  | Facility uses 100 gpd of glycerin in the 2nd anoxic zone.
Winchester | Parkins Mills WWTF | 158 West Parkins Mills Road, Winchester, VA 22602 | same | 540-6624475 | VA0075191 | M | Hank Sliwinski |  | 5 | Potomac River Basin | x | [6 empty] | x |  | x | x | x |  |  |  |  | Facility uses glycerin at 165 gallons per day.
Winchester | Opequon Water Rec Fac | 3100 Berryville Road Winchester, VA 22603 | same | 540-665-9867 | VA0065552 | M | Richard Watkins |  | 8.4 | Potomac River Basin | [5 empty] | x |  |  |  | x | x | x |  |  |  |  | Facility uses approx 120 gallons per day of 20% acetic acid for Bio P and 280 gpd glycerin for denitrification.
Woodbridge | HL MooneyWWTF | 1851 Rippon Blvd. Woodbridge, VA 22191 | same | 703-335-7904 | VA0025101 | M | John Sloper |  | 24 | Potomac River basin | x | x | [6 empty] | x | x |  |  |  |  | x | x | Large methanol user with denitrification filters with a 3 mg/l TN limit
30/30 85/85